## Schedule
SCHEDULE OF SPECIAL INSPECTION SERVICES
PROJECT | (Completed by the Registered Design Professional in Responsible Charge)
APPLICABLE TO THIS PROJECT
MATERIAL / ACTIVITY | SERVICE | Y/N | EXTENT | AGENT* | DATE COMPLETED
1705.1.1 Special Cases (work unusual in nature, including but not limited to alternative construction materials, unusual design applications, systems or materials with special manufacturer requirements. Attach 8 1/2x11 if needed). | Submittal review, shop(3) inspection and/or field inspection.
1705.2 Structural Steel Construction
1. Review the material test reports and certificates as listed in AISC 360-16, Section N3.2 for compliance with the construction documents | Submittal review |  | Each submittal
2. Material verification of structural steel | Shop (3) and field inspection |  | Periodic
3. Anchor Rods and other Embedment(s) (Verify diameter, grade, type, length, embedment. See 1705.3 for anchors) | Field inspection |  | Continuous
4. Verify member locations, braces, stiffeners, and application of joint details at each connection comply with construction documents | Field inspection |  | Periodic
5. Structural steel welding:
a. Inspection tasks Prior to Welding (Observe, or perform for each welded joint or member, the QA tasks listed in AISC 360, Table N5.4-1) | Shop (3) and field inspection |  | Observe or Perform as noted (4)
b. Inspection tasks During Welding (Observe, or perform for each welded joint or member, the QA tasks listed in AISC 360, Table N5.4-2) | Shop (3) and field inspection |  | Observe (4)
c. Inspection tasks After Welding (Observe, or perform for each welded joint or member, the QA tasks listed in AISC 360, Table N5.4-3) | Shop (3) and field inspection |  | Observe or Perform as noted (4)
d. Nondestructive testing (NDT) of welded joints: see Commentary
1) Complete penetration groove welds at joints in materials 5/16" thick or greater in Risk Category III or IV | Shop (3) or field ultrasonic testing - 100% |  | Periodic
2) Complete penetration groove welds at joints in materials 5/16" or greater in Risk Category II | Shop (3) or field ultrasonic testing - 10% of welds minimum |  | Periodic
3) Thermally cut surfaces of access holes when material t > 2" | Shop (3) or field magnetic Particle or Penetrant testing |  | Periodic
4) Welded joints subject to fatigue when required by AISC 360, Appendix 3, Table A-3.1 | Shop (3) or field radiographic or Ultrasonic testing |  | Periodic
5) Fabricator's NDT reports when fabricator performs NDT | Verify reports |  | Each submittal (5)
6. Structural steel bolting: | Shop (3) and field inspection
a. Inspection tasks Prior to Bolting (Observe, or perform tasks for each bolted connection, in accordance with QA tasks listed in AISC 360-16, Table N5.6-1) |  |  | Observe or Perform as noted (4)
b.Inspection tasks During Bolting (Observe the QA tasks listed in AISC 360-16, Table N5.6-2) |  |  | Observe (4)
1) Pre-tensioned and slip-critical joints
a) Turn-of-nut with matching markings |  |  | Periodic
b) Direct tension indicator |  |  | Periodic
c) Twist-off type tension control bolt |  |  | Periodic
d) Turn-of-nut without matching markings |  |  | Continuous
e) Calibrated wrench |  |  | Continuous
2) Snug-tight joints |  |  | Periodic
c. Inspection tasks After Bolting (Perform tasks for each bolted connection in accordance with QA tasks listed in AISC 360, Table N5.6-3) |  |  | Perform (4)
7. Inspection of steel elements of composite construction prior to concrete placement in accordance with SDI QA/QC tasks listed in Section 1705.2.2 for steel deck and AISC 360-16, Table N5.4-2 Section N5 for welding Headed stud anchors | Shop (3) and field inspection and testing |  | Observe or Perform as noted (4)
a. Placement and installation of steel headed stud anchors |  |  | Periodic
1705.2.2 Cold-formed Steel Deck (shall be performed according to the requirements of SDI QA/QC)
1. Inspection or Execution Tasks Prior and After Deck Placement according to Table 1.1 & 1.2 of SDI QA/QC:
a. Identification markings | Field inspection |  | Periodic
b. Manufacturer's certified test reports, deck profile and thickness | Submittal Review |  | Each submittal
c. Verify deck installation per construction documents | Field inspection |  | Periodic
2. Inspection Prior, During & After Welding of Steel Deck according to Table 1.3, 1.4 & 1.5 of SDI QA/AC:
a. Prior (Table1.3): Welding procedure Specifications (WPS) available, Manufacturer's certifications for welding consumables available, Material identification (type/grade), welding equipment check. | Field inspection |  | Periodic
b. During (Table 1.4): Qualified welders, Environmental Conditions, WPS followed | Field inspection |  | Periodic
c. After (Table 1.5): Verify size and location of welds, including support, sidelap, and perimeter welds | Field inspection |  | Periodic
d. After (Table 1.5): Welds meet visual acceptance criteria | Field inspection |  | Periodic
e. After (Table 1.5): Verify repair activities and Document acceptance or rejection of welds | Field inspection |  | Periodic
3. Inspection Prior, During & After Mechanical Fastening of Steel Deck according to Table 1.6, 1.7 & 1.8 of SDI QA/AC:
a. Prior (Table1.6): Manufacturer installation instructions available for mechanical fasteners, Proper tools available for fastener installation, Proper storage for mechanical fasteners | Field inspection |  | Periodic
b. During (Table 1.7): Fasteners are positioned as required and fasteners are installed according to manufacturer's instructions | Field inspection |  | Periodic
c. After (Table 1.8): Check spacing, type, and installation of support, sidelap, and perimeter fasteners. | Field inspection |  | Periodic
d. After (Table 1.8): Verify repair activities and Document acceptance or rejection of mechanical fasteners | Field inspection |  | Periodic
1705.2.3 Open-web Steel Joist and Joist Girders (Table 1705.2.3)
1. Installation of open-web steel joists and joist girders.
a. End connections - welding or bolted | Field inspection |  | Periodic
b. Bridging - horizontal or diagonal | Field inspection |  | Periodic
1705.2.4 Cold-formed Steel Trusses spanning 60 feet or greater
1. Verify temporary and permanent restraint/bracing are installed in accordance with the approved truss submittal package. | Field inspection |  | Periodic
1705.3 Concrete Construction
1. Inspection of reinforcement, including prestressing tendons, and verify placement. Placement includes reinforcing bar size, shape, spacing, cover, embedment, orientation, bar length, and splices per the construction documents and approved placement drawings. | Field inspection |  | Periodic
2. Reinforcing bar welding
a. Verify weldability of reinforcing bars other than ASTM A706 | Field inspection |  | Periodic
b. Inspect single-pass fillet welds, maximum 5/16" | Field inspection |  | Periodic
c. Inspect fillet welds >5/16" and other weld types | Field inspection |  | Continuous
3. Inspection of anchors cast in concrete | Shop (3) and field inspection |  | Periodic
4. Inspection of anchors and reinforcing steel post-installed in hardened concrete: Per research reports requirements | Field inspection |  | Periodic or as required by the research report issued by an approved source
a. Adhesive anchors installed horizontally or in upwardly inclined orientations to resist sustained tension loads. | Field inspection |  | Continuous
b. Mechanical anchors and adhesive anchors not defined in 4.a. | Field inspection |  | Periodic
5. Verify use of approved design mix | Shop (3) and field inspection |  | Periodic
6. Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests and determine temperature of concrete | Shop (3) and field inspection |  | Continuous
7. Inspection of concrete and shotcrete placement for proper application techniques | Shop (3) and field inspection |  | Continuous
8. Inspection for maintenance of specified curing temperature and techniques | Shop (3) and field inspection |  | Periodic
9. Inspection of prestressed concrete: | In-plant or field review
a. Application of prestressing forces |  |  | Continuous
b. Grouting of bonded prestressing tendons in the seismic-force-resisting system |  |  | Continuous
10. Inspect erection of precast concrete members | Field inspection |  | Periodic
11. For precast concrete diaphragm connections or reinforcement at joints classified as moderate or high deformability elements (MDE or HDE) in structures assigned to Seismic Design Category C, D, E or F, inspection such connections and reinforcement for:
a. Installation of the embedded parts | Field inspection |  | Continuous
b. Completion of the continuity of reinforcement across joints | Field inspection |  | Continuous
c. Completion of connections in the field. | Field inspection |  | Continuous
12. Inspect installation tolerances of precast concrete diaphragm connections for compliance with ACI 550.5 | Field inspection |  | Periodic
13. Verification of in-situ concrete strength, prior to stressing of tendons in post tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | Field testing and review of laboratory reports |  | Periodic
14. Inspection of formwork for shape, lines, location and dimensions | Field inspection |  | Periodic
15. Concrete strength testing and verification of compliance with construction documents | Field testing and review of laboratory reports |  | Periodic
16. For post-tensioned concrete, inspect cutting of tendon tail, installation of encapsulation cap and filling of stressing pocket in accordance with the construction documents and the post tensioning installation drawings. | Field inspection |  | Continuous
1705.4 Masonry Construction
(A) Level 1, 2 and 3 Quality Assurance:
1. Prior to constructuction, verification of compliance of submittals | Submittal review |  | Periodic
(B) Level 2 Quality Assurance:
1. Verification of f'm and f'AAC prior to construction | Testing by unit strength method or prism test method |  | Periodic
(C) Level 3 Quality Assurance:
1. Verification of f'm and f'AAC prior to construction and for every 5,000 SF during construction | Testing by unit strength method or prism test method |  | Periodic
2. Verification of proportions of materials in premixed or preblended mortar, prestressing grout, and grout other than selfconsolidating grout, as delivered to the project site | Field inspection |  | Continuous
(D) Levels 2 and 3 Quality Assurance:
1. Verification of Slump Flow and Visual Stability Index (VSI) of selfconsolidating grout as delivered to the project | Field testing |  | Continuous
2. Verify proportions of site-mixed mortar, grout and prestressing grout for bonded tendons | Field Inspection |  | Periodic
3. Verify location, grade, type, and size of reinforcement and anchor bolts, and prestressing tendons and anchorages | Field Inspection |  | Periodic
4. Verify prestressing technique | Field Inspection |  | Periodic
5. Verify sample panel construction | Field Inspection |  | Periodic
6. Verify placement of masonry units and mortar joint construction | Field Inspection |  | Periodic
7. Verify placement of reinforcement, connectors, and prestressing tendons and anchorages | Field Inspection |  | Level 2 - Periodic
Level 3 - Continuous
8. Verify grout space prior to grouting | Field Inspection |  | Level 2 - Periodic
Level 3 - Continuous
9. Verify placement of grout and prestressing grout for bonded tendons | Field Inspection |  | Continuous
10. Verify size and location of structural members | Field Inspection |  | Periodic
11. Verify type, size, and location of anchors, including details of anchorage of masonry to structural members, frames, or other construction. | Field inspection |  | Level 2 - Periodic
Level 3 - Continuous
12. Verify welding of reinforcement (see 1705.3.1) | Field inspection |  | Continuous
13. Verify preparation, construction, and protection of masonry during cold weather (temperature below 40o F) or hot weather (temperature above 90o F) | Field inspection |  | Periodic
14. Verify application and measurement of prestressing force | Field Inspection |  | Continuous
15. Verify placement of AAC masonry units and construction of thin-bed mortar joints (first 5000 SF of AAC masonry) | Field inspection |  | Continuous
16. Verify placement of AAC masonry units and construction of thin-bed mortar joints (after the first 5000 SF of AAC masonry) | Field inspection |  | Level 2 - Periodic
Level 3 - Continuous
17. Verify properties of thin-bed mortar for AAC masonry (first 5000 SF of AAC masonry) | Field inspection |  | Continuous
18. Verify properties of thin-bed mortar for AAC masonry (after the first 5000 SF of AAC masonry) | Field inspection |  | Level 2 - Periodic
Level 3 - Continuous
19. Verify compliance of materials and procedures with the approved submittals | Field inspection |  | Periodic
20. Observe preparation of grout specimens, mortar specimens, and/or prisms | Field inspection |  | Level 2 - Periodic
Level 3 - Continuous
1705.5 Wood Construction
1. Inspection of the fabrication process of wood structural elements and assemblies in accordance with Section 1704.2.5 | In-plant review (3) |  | Periodic
2. For high-load diaphragms, verification of grade and thickness of structural panel sheathing. | Field inspection |  | Periodic
3. For high-load diaphragms, verify nominal size of framing members at adjoining panel edges, nail or staple diameter and length, number of fastener lines, and that spacing between fasteners in each line and at edge margins agrees with approved construction documents. | Field inspection |  | Periodic
4. Metal-plate-connected wood trusses with overall heights of 60 inches or greater inspection shall be performed to verify that the installation of the permanent individual truss member restraint/bracing has been installed in accordance with the approved truss submittal package. | Field Inspection |  | Periodic
5. Metal-plate-connected wood trusses with a clear span of 60 feet or greater, the special inspector shall verify during construction that the temporary installation restraint/bracing is installed in accordance with the approved truss submittal package. | Field inspection |  | Continuous
6.Mass timber construction for elements in types IV-A, IV-B, and IV-C construction | Field inspection |  | Continuous
a. Inspection of anchorage and connections of mass timber construction to timber deep foundation systems. | Field inspection |  | Periodic
b. Inspect erection of mass timber construction | Field Inspection |  | Periodic
c. Inspection of connections where installation methods are required to meet design loads.
i. Threaded fasteners
ia. Verify use of proper installation equipment | Field inspection |  | Periodic
ib. verify use of pre-drilled holes where required | Field inspection |  | Periodic
ic. Inspect screws, including diameter, length, head type, spacing, installation angle and depth | Field inspection |  | Periodic
ii. Adhesive anchors installed in horizontal or upwardly inclined orientation to resist sustained tension loads | Field inspection |  | Continuous
iii. Adhesive anchors not defined in preceding cell | Field inspection |  | Periodic
iv. Bolted connections | Field inspection |  | Periodic
v. Conceaed connections | Field inspection |  | Periodic
1705.6 Soils
1. Verify materials below shallow foundations are adequate to achieve the design bearing capacity. | Field inspection |  | Periodic
2. Verify excavations are extended to proper depth and have reached proper material. | Field inspection |  | Periodic
3. Perform classification and testing of controlled fill materials. | Field inspection |  | Periodic
4. During fill placement, verify use of proper materials and procedures in accordance with the provisions of the approved geotechnical report. Verify densities, and lift thicknesses during placement and compaction of compacted fill | Field inspection |  | Continuous
5. Prior to placement of controlled fill, observe subgrade and verify that site has been prepared properly | Field inspection |  | Periodic
1705.7 Driven Deep Foundations
1. Verify element materials, sizes and lengths comply with requirements | Field inspection |  | Continuous
2. Determine capacities of test elements and conduct additional load tests, as required | Field inspection |  | Continuous
3. Inspect driving operations and maintain complete and accurate records for each element | Field inspection |  | Continuous
4. Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achieve design capacity, record tip and butt elevations and document any damage to foundation element | Field inspection |  | Continuous | `
5. For steel elements, perform additional inspections per Section 1705.2 | See Section 1705.2 |  | See Section 1705.2
6. For concrete elements and concrete-filled elements, perform additional inspections per Section 1705.3 | See Section 1705.3 |  | See Section 1705.3
7. For specialty elements, perform additional inspections as determined by the registered design professional in responsible charge | Field inspection |  | In accordance with Statement of Special Inspections
1705.8 Cast-in-Place Deep Foundations
1.Inspect drilling operations and maintain complete and accurate records for each element | Field inspection |  | Continuous
2. Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity. Record concrete or grout volumes | Field inspection |  | Continuous
3. For concrete elements, perform additional inspections in accordance with Section 1705.3 | See Section 1705.3 |  | See Section 1705.3
1705.9 Helical Pile Foundations
1. Verify installation equipment, pile dimensions, tip elevations, final depth, final installation torque and other data as required | Field inspection |  | Continuous
2. Perform additional inspections and tests in accordance with the construction documents | Field Inspection and testing |  | In accordance with construction documents
1705.11 Fabricated Items
Inspection of fabricated items shall be performed in accordance with Section 1704.2.5
1. List of fabricated items requiring special inspection during fabrication: | Shop Inspection
2. List of fabricated items to be fabricated on the premesis of a fabricator approved to perform such work without special inspection:
1705.12.1 Structural Wood Special Inspections For Wind (Tornado) Resistance
1. Inspection of field gluing operations of elements of the main windforce-resisting system | Field inspection |  | Continuous
2. Inspection of nailing, bolting, anchoring and other fastening of elements of the main windforce-resisting system | Shop (3) and field inspection |  | Periodic
1705.12.2 Cold-formed Steel Special Inspections For Wind (Tornado) Resistance
1.Inspection during welding operations of elements of the main windforce-resisting system | Shop (3) and field inspection |  | Periodic
2.Inspections for screw attachment, bolting, anchoring and other fastening of elements of the main windforce-resisting system | Shop (3) and field inspection |  | Periodic
1705.12.3 Wind-resisting Components
1. Roof covering, roof deck and roof framing connections | Shop (3) and field inspection |  | Periodic
2. Exterior wall covering and wall connections to roof and floor diaphragms and framing. | Shop (3) and field inspection |  | Periodic
1705.13.1 Structural Steel Special Inspections for Seismic Resistance
1. Fabricator and erector documents (Verify reports and certificates as listed in AISC 341-16,Section J2 for compliance with construction documents) | Submittal Review |  | Each submittal
2. Structural steel welding:
a. Inspection tasks Prior to, During and After Welding (Observe, or perform for each welded joint or member, the QA tasks listed in AISC 341-16, Table J6.1, J6.2 & J6.3) | Shop (3) and field inspection |  | Observe or Perform as noted (4)
b. Nondestructive testing (NDT) of welded joints in accordance with AISC 341-16, Section J6.2. | Shop (3) and field testing |  | Periodic
3. Structural steel bolting:
a. Inspection tasks Prior to, During and After Bolting (Observe, or perform tasks for each bolted connection, in accordance with QA tasks listed in AISC 341-16, Table J7.1, J7.2 & J7.3) | Shop (3) and field inspection |  | Observe or Perform as noted (4)
4. Other Steel Structure Inspections, in accordance with QA tasks listed in AISC 341-16, Table J8.1:
a. RBS requirements | Shop (3) and field inspection |  | Observe (4)
b. Protected zones | Shop (3) and field inspection |  | Observe (4)
5. Composite construction:
a. Inspection tasks Prior to, During and After Concrete Placement (Observe, or perform tasks, in accordance with QA tasks listed in AISC 341-16, Table J9.1, J9.2 & J9.3) | Field inspection |  | Observe (4)
6. H-Piling:
a. Inspection of H-piling in accordance with AISC 341-16, Table J10.1 | Field Inpsection |  | Periodic
1705.13.2 Structural Wood Special Inspections for Seismic Resistance
1. Inspection of field gluing operations of elements of the seismic-force resisting system | Field inspection |  | Continuous
2. Inspection of nailing, bolting, anchoring and other fastening of components within the seismic-force-resisting system | Shop (3) and field inspection |  | Periodic
1705.13.3 Cold-formed Steel Light-Frame Construction Special Inspections for Seismic Resistance
1. Inspection during welding operations of elements of the seismic force-resisting system | Shop (3) and field inspection |  | Periodic
2. Inspections for screw attachment, bolting, anchoring and other fastening of components within the seismic force-resisting system | Shop (3) and field inspection |  | Periodic
1705.13.4 Designated Seismic System Verification
Inspect and verify that the component label, anchorage or mounting conforms to the certificate of compliance in accordance with 13.2.2 of ASCE 7-16 | Field inspection |  | Periodic
1. Architectural Designated Seismic Systems (per ASCE 7-16)
a. Interior non-structural partition walls and connections | Field Inspection |  | Periodic
b. Parapets | Field Inspection |  | Periodic
c. Chimneys | Field Inspection |  | Periodic
d. Exterior non-structural walls elements and connections | Field Inspection |  | Periodic
e. Veneer | Field Inspection |  | Periodic
f. Suspended Ceiling Systems | Field Inspection |  | Periodic
g. Cabinets | Field Inspection |  | Periodic
h. Storefront and curtainwall framing | Field Inspection |  | Periodic
i. Access Floors | Field Inspections |  | Periodic
j. Glass in glazed interior and exterior storefront and curtainwall systems | Field Inspection |  | Periodic
k. Laboratory Equipment | Field Inspection |  | Periodic
2. Mechanical & Electrical Designated Seismic Systems (per ASCE 7-16)
a. Mechanical and Electrical Components
1) Air-side HVAC fans, air handlers, air conditioning units, cabinet heaters, air distribution boxes, and other mechanical components constructed of sheet metal framing | Field Inspection |  | Periodic
2) Wet side HVAC, boilers, furnaces, atmospheric tanks and bins, chillers, water heaters, heat exchangers, evaporators, air separators, manufacturing or process equipment and other mechanical components constructed of high-deformability materials | Field Inspection |  | Periodic
3) Engines, turbines, pumps, compressors, and pressure vessels | Field Inspection |  | Periodic
4) Elevator and escalator components | Field Inspection |  | Periodic
5) Generators, batteries, invertors, motors, transformers, and other electrical components constructed of high deformability materials | Field Inspection |  | Periodic
6) Motor control centers, panel boards, switch gear, instrumentation cabinets, and other components constructed of sheet metal framing | Field Inspection |  | Periodic
7) Communication equipment, computers, instrumentation and controls | Field Inspection |  | Periodic
8) Roof mounted stacks, cooling and electical towers | Field Inspection |  | Periodic
9) Light fixtures | Field Inspection |  | Periodic
b. Vibration Isolated Components & Systems
1) Components and systems isolated using neoprene elements and neoprene isolated floors with built-in or separate elastomeric snubbing devices or resilient perimeter stops | Field Inspection |  | Periodic
2) Spring isolated components and systems closely restrained using built in or separate elastomeric snubbing devices or resilient perimeter stops | Field Inspection |  | Periodic
3) Internally isolated systems and supports | Field Inspection |  | Periodic
4) Suspended vibration isolation equipment including in-line duct devices and suspended internally isolated components | Field Inspection |  | Periodic
c. Distribution Systems
1) Piping and tubing including in-line components | Field Inspection |  | Periodic
2) Ductwork, including in–line components | Field Inspection |  | Periodic
3) Electrical conduit and cable trays | Field Inspection |  | Periodic
4) Bus ducts
5) Plumbing | Field Inspection |  | Periodic
6) Pneumatic tube transport systems | Field Inspection |  | Periodic
7) Fire Protection Sprinkler Pipe System | Field Inspection |  | Periodic
1705.13.5 Architectural Components Special Inspections for Seismic Resistance
1. Inspection during the erection and fastening of exterior cladding and interior and exterior veneer. | Field inspection |  | Periodic
2. Inspection during the erection and fastening of interior and exterior non load bearing walls. | Field inspection |  | Periodic
3. Inspection during anchorage of access floors | Field inspection |  | Periodic
1705.13.6 Plumbing, Mechanical and Electrical Components Special Inspections for Seismic Resistance
1. Inspection during the anchorage of electrical equipment for emergency or standby power systems. | Field inspection |  | Periodic
2. Inspection during the anchorage of other electrical equipment. | Field inspection |  | Periodic
3. Inspection during installation and anchorage of piping systems designed to carry hazardous materials, and their associated mechanical units | Field inspection |  | Periodic
4. Inspection during the installation and anchorage of ductwork designed to carry hazardous materials | Field inspection |  | Periodic
5. Inspection during the installation and anchorage of vibration isolation systems. | Field inspection |  | Periodic
6. Inspection during the installation of mechanical and electrical equipment, including duct work, piping systems and their structural supports, where automatic fire sprinkler systems are installed to verify on of the following:
a. Minimum clearances have been provided as required by Section 13.2.3 ASCE 7 | Field inspection |  | Periodic
b. A nominal clearance of not less than 3 inches has been provided between fire protection sprinkler system drops and sprigs and; structural members not used collectively or independently to support the sprinklers; equipment attached to the building structure; and other systems piping | Field inspection |  | Periodic
1705.13.7 Storage Racks for Seismic Resistance
Steel storage racks 8 feet or greater in height
1. Materials used, to verify compliance with one or more of the material test reports in accordance with the approved construction documents | Field inspection |  | Periodic
2. Fabricated storage rack elements. | Field inspection |  | Periodic
3. Storage rack anchorage installation. | Field inspection |  | Periodic
4. Completed storage rack system, to indicate compliance with the approved construction documents | Field inspection |  | Periodic
1705.13.9 Cold-formed Steel Special Bolted Moment Frames
Inspection during the installation of cold-formed steel special bolted moment frames | Shop and field inspection |  | Periodic
1705.14.1 Structural Steel Testing and Qualification for Seismic Resistance
Test structural steel in the seismic force-resisting system in accordance with the quality assurance requirements of AISC 341 | Shop (3) and field testing |  | Per AISC 341
1705.14.2 Seismic Certification of Nonstructural Components
Review certificate of compliance for designated seismic system components. | Certificate of compliance review |  | Each submittal
1705.14.4 Seismic Isolation Systems
Test seismic isolation system in accordance with ASCE 7 Section 17.8 | Prototype testing |  | Per ASCE 7
1705.15 Sprayed Fire-resistant Materials
1. Verify surface condition preparation of structural members. | Field inspection |  | Periodic
2. Verify application of sprayed fire-resistant materials. | Field inspection |  | Periodic
3. Verify average thickness of sprayed fire-resistant materials applied to structural members. | Field inspection |  | Periodic
4. Verify density of the sprayed fire-resistant material complies with approved fire-resistant design. | Field inspection and testing |  | Per Building Code section 1705.15.5
5. Verify the cohesive/adhesive bond strength of the cured sprayed fire-resistant material. | Field inspection and testing |  | Per Building Code section 1705.15.6
1705.16 Mastic and Intumescent Fire-Resistant Coatings
Inspect mastic and intumescent fire-resistant coatings applied to structural elements and decks, in accordance with AWCI 12-B. | Field inspection |  | Periodic
1705.17 Exterior Insulation and Finish Systems (EIFS)
1. Verify materials, details and installations are per the approved construction documents | Field inspection |  | Periodic
2. Inspection of water-resistive barrier coating over sheathing substrate | Field inspection |  | Periodic
1705.18 Fire-Resistant Penetrations and Joints
1. Inspect penetration firestop | Field testing |  | Per ASTM E 2174
2. Inspect fire-resistant joint systems | Field testing |  | Per ASTM E 2393
1705.19 Smoke Control Systems
1. Leakage testing and recording of device locations prior to concealment. | Field testing |  | Periodic
2. Prior to occupancy and after sufficient completion, pressure difference testing, flow measurements, and detection and control verification. | Field testing |  | Periodic
1705.20 Sealing of mass timber
1. Inspect sealants or adhesive application where required by Section 703.7 | Field testing |  | Periodic
* INSPECTION AGENTS | FIRM |  | ADDRESS |  | TELEPHONE NO.
1.
2.
3.
4.
5.
Notes: 1. The inspection and testing agent(s) shall be engaged by the Owner or the Owner's Agent, not by the Contractor or Subcontractor whose work
is to be inspected or tested. Any conflict of interest must be disclosed to the Building Official prior to commencing work. The qualifications of the
Special Inspector(s) and/or testing agencies are subject to the approval of the Building Official and/or the Design Professional.
2. The list of Special Inspectors may be submitted as a separate document, if noted so above.
3. Special Inspections as required by Section 1704.2.5 are not required where the fabricator is approved in accordance with IBC Section 1704.2.5.1
4. Observe on a random basis, operations need not be delayed pending these inspections. Perform these tasks for each welded joint, bolted
connection, or steel element.
5. NDT of welds completed in an approved fabricator's shop may be performed by that fabricator when approved by the AHJ. Refer to AISC 360, N7.
Circle "Yes" or "No" as appropriate and date this document below:
Are Requirements for Seismic Resistance included in the Statement of Special Inspections? |  |  |  | Yes No
Are Requirements for Tornado Resistance included in the Statement of Special Inspections? |  |  |  | Yes No
DATE: